## PD Dataset Catalog
# | Dataset Name | Source / Authors | PD Types / Labels | Sensor Type (HFCT is priority) | Sample Rate >80 MSPS only | Sample Count / Volume | File Format | Data Type Description (50/60 Hz) | Size | Access | License | URL | Key Relevance Notes | Asset Type
1 | UFCG Controlled Partial Discharge Database | Melo, de Lira, da Costa, Vilar, Leite Neto — UFCG High-Voltage Lab (Campina Grande, Brazil). Published June 2025. | Corona (2 needle-to-plane configs, 100 acq) Surface (rain on insulator, 50 acq) Internal–solid (oil-filled cell, 50 acq) Internal–liquid (oil reservoir, 50 acq) | HFCT (1–80 MHz linear response). UV camera (Ofil SN 213) verified discharge types. | 125 MSa/s | 250 acquisitions (35 ms windows), 4 channels each (CH1=PD, CH2=voltage, CH3/CH4=additional) | .mat (MATLAB v5 binary) | Raw time-domain waveform arrays. Each .mat file contains 4-channel numerical arrays of voltage vs. time. Loadable via scipy.io.loadmat in Python or MATLAB. Organized in folders by discharge type. | 8.39 GB | IEEE DataPort subscription (free for IEEE members) | IEEE DataPort Terms | https://ieee-dataport.org/documents/database-different-sources-controlled-partial-discharges | Closest match to Magnefy setup: same HFCT sensor, identical 125 MSa/s sample rate, labeled multi-class PD. Only gap is no dedicated noise class (extract from signal backgrounds). START HERE. | Transformer
2 | VSB-TUO PD vs Corona High-Resolution Antenna Dataset | Kabot et al., VŠB–TU Ostrava. Nature Scientific Data 12, 1361 (Aug 2025). DOI: 10.1038/s41597-025-05627-z | 5 discharge classes: PD, Corona, Mixed PD+Corona, High-impedance PD variant, High-impedance Corona variant + 2 background conditions (with/without HV) | Contactless dual-antenna system | 500 MSa/s | ~1,400 signals (100 per class × 5 types × 2 antennas + backgrounds). 10⁷ data points per 20 ms window. | .bin (binary), convertible to .npy | High-resolution raw voltage waveforms stored as binary floating-point arrays. Python loader scripts provided on GitHub. Each sample = 20 ms capture window with 10 million data points. Dual-antenna captures give two simultaneous perspectives. | Not specified (large — 10⁷ pts × ~1,400 signals) | Open access, free download | CC BY 4.0 | https://doi.org/10.6084/m9.figshare.28523090 GitHub: https://github.com/Lukykl1/dataset_pd_corona_vsb | Designed for ML. Peer-reviewed in Nature. Very recent (2025). PD vs corona discrimination directly relevant. 500 MSa/s can be downsampled to match Magnefy's 125 MSa/s. Antenna ≠ HFCT but similar EM signatures. | XLPE-covered conductors utilized in medium-voltage overhead power distribution lines
3 | VSB Power Line Fault Detection (Kaggle Competition) | ENET Centre, VŠB–TU Ostrava (Czechia) | Binary: PD present (1) vs no PD (0). ~6% positive class (highly imbalanced). | Custom ENET Centre contactless antenna on MV overhead lines | 40 MSa/s | 8,712 training + 20,337 test = ~29,000 signals. 800,000 measurements per signal (one 50 Hz cycle). | Apache Parquet (.parquet) | Columnar binary format storing integer voltage samples. Each signal = 800k data points representing one 20 ms AC cycle. Metadata CSV with signal_id, phase (A/B/C), and binary target. Parquet is efficient for large columnar reads (pandas, pyarrow). | ~45 GB | Free with Kaggle account | Kaggle competition terms | https://www.kaggle.com/c/vsb-power-line-fault-detection/data GitHub baseline: https://github.com/tvhahn/PD-Deep | Largest public PD dataset by sample count. Binary only (not multi-class). Excellent for pipeline prototyping. 1,647 teams competed — extensive community solutions. Imbalanced data mirrors real field conditions. | Power line
4 | Figshare PD & Noise Signal Dataset (Electrical Machines) | Rauscher et al., "Deep learning and data augmentation for PD detection in electrical machines," Eng. Applications of AI, 133, 108074 (2024) | Binary: PD vs NonPD (noise) | EM/inductive PD sensor on automotive traction machine production lines | Not specified - "sampling frequency of 10 GHz" | Pre-split: Train (Tr0, Tr1), Validation (Va0, Va1), Test (Te0, Te1, Te2) | Downloadable data files (numerical arrays) | Pre-processed PD and noise signal segments, already split into train/validation/test partitions. Ready for direct ML training without preprocessing. Companion paper includes data augmentation code achieving 99.76% accuracy. | Not specified | Open access, free download | CC BY 4.0 | https://figshare.com/articles/dataset/Dataset_of_partial_discharge_and_noise_signals/24033225 | Clean, research-ready, pre-split. PD vs noise task directly relevant to Phase 3 noise floor analysis. Paper includes augmentation techniques to reference. | automotive traction machine production lines
5 | IEEE DataPort — PD Detection (Rotating Machinery) | Pinardi, Toscani, Immovilli — University of Parma (2024). DOI: 10.21227/57zj-4y32 | PD monitoring signals at varying voltage levels | Full-digital PD monitoring device with HFCT front-end | LeCroy oscilloscope at 20 MHz or DAQ at 48 kHz | 9 measurements per series at voltage levels 1.0–2.0 kV | .wav (2-channel audio) | Two-channel WAV files: Channel 1 = PD signal, Channel 2 = 50 Hz reference. Standard audio format readable by scipy.io.wavfile, librosa, or any audio tool. Low-cost modular monitoring architecture. | Not specified | IEEE DataPort subscription | IEEE DataPort Terms | https://ieee-dataport.org/documents/partial-discharge-detection | HFCT→digital→cloud architecture mirrors Magnefy's pipeline. Asset type differs (motors vs transformers) but signal processing methodology is transferable. | rotating machinery
6 | VSB Overhead Line Antenna Dataset — 3 Years Field Data | Klein et al., VŠB–TU Ostrava. Nature Scientific Data 10, 544 (2023). DOI: 10.1038/s41597-023-02451-1 | PD detection with expert-curated annotations + galvanic contact ground truth | Contactless wireless antenna on XLPE-covered MV lines; 8-bit ADC (−128 to 127) | Not specified (8-bit ADC) - 40 MS/s | ~3 years of hourly measurements from 9 monitoring stations. Each sample = 20 ms signal window. | .npy (NumPy binary arrays) + .csv metadata | NumPy arrays of 8-bit integer voltage samples per time window. CSV files contain station metadata, timestamps, and expert annotations. Python loader utilities on GitHub. 8-bit resolution is lower than Magnefy but noise challenges are identical. | Not specified (very large — 3 years × 9 stations × hourly) | Open access, free download | CC BY | https://doi.org/10.6084/m9.figshare.c.6628553.v1 GitHub: https://github.com/Lukykl1/dataset_pd_vsb | Massive longitudinal real-world data. Annotation methodology (expert + secondary sensor ground truth) is a model for Magnefy field validation. Used in 2025 synthetic data pretraining paper. Excellent for pretraining and noise characterization. | XLPE-covered MV lines
7 | VSB Fault Types in Covered Conductors | Kabot et al., VŠB–TU Ostrava. Nature Scientific Data 11, 1319 (2024). DOI: 10.1038/s41597-024-04009-1 | 12 distinct fault categories (ground phase faults, inter-phase faults, no-fault) | 3 different antenna types | Not specified - 500 MHz | 10⁶ data points per sample across fault categories | Floating-point numerical data files | High-precision floating-point waveform samples (10⁶ points each). Multi-antenna captures from 3 different antenna designs. 12-class labeling system for detailed fault taxonomy. | Not specified | Open access via Figshare | CC BY 4.0 (assumed, Figshare) | https://doi.org/10.6084/m9.figshare.26946910 | Multi-class fault classification with high-quality labels. Good for transfer learning approaches. Complements other VSB datasets. | 22 kV Voltage Power Lines
8 | Mendeley — GIS PD Pattern Recognition (PRPD) | Wu et al., 550 kV GIS experiments | Corona (C-type, 280 patterns) Surface (S-type, 129 patterns) Floating electrode (F-type, 9 patterns) = 418 total PRPD patterns | Omicron MPD600 | N/A (phase-resolved patterns, not raw waveforms) | 418 PRPD patterns | Tabular (Φ, Q, N) tuples | Phase-Resolved Partial Discharge data: each record is a (phase angle Φ, charge magnitude Q, pulse count N) tuple. NOT raw time-domain waveforms. Useful for understanding phase-domain classification targets and benchmarking feature extraction. | Small | Open access, free download | Mendeley Data terms | https://data.mendeley.com/datasets/cz8gwg9d2v/1 | PRPD patterns, not raw waveforms. Useful for phase-domain understanding. Authors call for open-sourcing more PD data — worth citing. Ask Derrick if Magnefy uses Omicron MPD600 or similar. | GIS (gas insulated switchgear?)
9 | Mendeley — PRPD Images from Colombian Generators | Zorrilla Henao et al., Data in Brief (2023). DOI: 10.1016/j.dib.2023.109878. 40+ generators in Colombia + Omicron simulator. | Internal, Corona, Surface + Noise images ✅ Only dataset with ALL 4 target classes | Coupling capacitors (2 nF) per IEC 60034-27, Omicron MPD 600 | N/A (PRPD images) | Multiple generators × 3 PD classes + noise (augmented for diversity) | .png images (570×440 px, RGB) | Phase-resolved partial discharge pattern images in PNG format. Each image is a 570×440 pixel RGB color plot showing phase angle vs. charge magnitude density. NOT raw waveforms. Suitable for CNN-based image classification or transfer learning. IEC 60270 / IEEE 1434 compliant measurements. | Not specified | Open access via Mendeley Data | CC BY 4.0 | https://pmc.ncbi.nlm.nih.gov/articles/PMC10827395/ | ONLY dataset covering all 4 target classes (internal, corona, surface, noise). Image-based, not waveform. Good for CNN approaches and transfer learning foundation. Real field data from operational generators. | generators
10 | PD-Loc Acoustic Localization Dataset | South East Technological University, Ireland. DOI: 10.21227/yy7g-2p79 | Chirps, white Gaussian noise, PD signals — by signal type and spatial location | 32-channel acoustic array (MEMS ICS40180 + electret condenser MAX9814) | 96 kHz | 9 configs × 90 fault locations × 18 stator coils × 3 signal types × 32 channels | .wav audio files | Multi-channel audio WAV files at 96 kHz. Each file = one microphone channel capturing acoustic emissions from PD events. 32 simultaneous channels provide spatial information for localization. Standard audio format, easy to load. | Not specified | Open Access (free with IEEE login, no subscription) | IEEE DataPort Open Access | https://ieee-dataport.org/open-access/partial-discharge-localisation-pd-loc-dataset | Acoustic, not EM. Useful for PD localization techniques and multimodal fusion (Project 2 in SOW). 32-sensor array demonstrates multi-sensor spatial capture. | "electric machines"
11 | IEEE DataPort — DGA in Transformer Oil | Enwen Li (2019). DOI: 10.21227/h8g0-8z59 | Fault types based on dissolved gas ratios (H₂, CH₄, C₂H₆, C₂H₄, C₂H₂) | Chemical / gas chromatography | N/A (tabular chemical data) | 3,147 instances, 4 fault classes | Tabular (CSV-like) | Each row = one oil sample with gas concentration columns (H₂, CH₄, C₂H₆, C₂H₄, C₂H₂) and a fault-type label. Standard tabular format for classical ML (SVM, random forest, etc.). NOT electromagnetic signal data. | Small | IEEE DataPort subscription | IEEE DataPort Terms | https://ieee-dataport.org/documents/dissolved-gas-data-transformer-oil-fault-diagnosis-power-transformers-membership-degree | DGA is the traditional method Magnefy augments/replaces. Cross-validate EM classifications against DGA fault categories. Context for 'why real-time EM sensing beats 6-month DGA sampling.'
12 | IEC TC 10 DGA Database | IEC Technical Committee 10 | PD, D1 (low energy discharge), D2 (high energy), T1/T2/T3 (thermal faults) | Chemical / gas chromatography | N/A (tabular chemical data) | ~134 fault samples | Varies (reproduced in academic literature) | Benchmark reference DGA dataset. Tabular gas ratio data with fault-type labels. Not freely hosted online but widely reproduced in published papers and available through IEEE DataPort compilations. | Small | Via academic literature / IEEE compilations | IEC | N/A (search academic literature) | Gold standard for DGA fault classification. Cross-reference these fault categories with EM-based PD classifications for validation.
13 | IEEE DataPort — Transformer Faults & Transients (Open Access) | IEEE DataPort. DOI: 10.21227/1d1w-q940 | Internal faults + transient events | Simulated (PSCAD/EMTDC) | Simulation time-step dependent | 88,128 internal fault files + 12,780 transient files = 100,908 total | Simulation output files | PSCAD/EMTDC electromagnetic transient simulation outputs. Each file represents one simulated fault or transient scenario in a power transformer model. Large-scale synthetic dataset for fault vs. transient discrimination. | 867 MB | Open access | IEEE DataPort Open Access | https://ieee-dataport.org (DOI: 10.21227/1d1w-q940) | Largest open transformer fault dataset found. Simulation-based but extensive fault scenarios. Useful for fault vs transient discrimination.
14 | Kaggle — Failure Analysis in Power Transformers | Kaggle community dataset | Multi-sensor fault labels (thermal, oil, gas) | OTI, WTI, OLI, MOGA (thermal/oil/gas sensors) | N/A (tabular sensor readings) | Tabular dataset | .csv | CSV file with columns for multiple sensor readings (Oil Temperature Indicator, Winding Temperature Indicator, Oil Level Indicator, Multi-gas Online Gas Analyzer) and fault-type labels. Standard tabular ML format. | Small | Free, open | Kaggle terms | https://www.kaggle.com/datasets/shashwatwork/failure-analysis-in-power-transformers-dataset | Different modality (thermal/oil). Useful for broader fault taxonomy understanding and potential multimodal fusion benchmarking. | Power Transformers
15 | Kaggle DGA Datasets (Multiple) | Various Kaggle contributors | DGA-based fault classification | Chemical / gas chromatography | N/A (tabular) | Varies | .csv | Standard CSV files with dissolved gas concentration columns and fault labels. Multiple datasets available: 'Dissolved Gas Analysis of Transformer' (Banti Patel), 'Power Transformers FDD and RUL' (Yuriy Katser). | Small | Free, open | Kaggle terms | https://www.kaggle.com/datasets/bantipatel20/dissolved-gas-analysis-of-transformer https://www.kaggle.com/datasets/yuriykatser/power-transformers-fdd-and-rul | Supplementary DGA data for comparative analysis with EM-based PD classification. | Dissolved gas analysis of transformer
16 | University of Strathclyde — LEMKE PD Measurements | EPSRC Centre for Doctoral Training, University of Strathclyde. DOI: 10.15129/64853769-2b98-49fb-afd9-0a857a0ca392 | PD in insulating materials (LDPE, polypropylene, XLPE films) | LEMKE LDS-6 (IEC 60270 compliant) | N/A (event-based: magnitude, phase, period) | 16 files (1 KB to 26 MB each) | ASCII text files | Plain text ASCII files containing PD event records: each line = one PD pulse with magnitude, phase angle, and period number. Both AC and DC conditions. Easy to parse with any programming language. IEC 60270 compliant measurements. | Small (KB to MB range) | Open (institutional repository) | Institutional | https://pureportal.strath.ac.uk/en/datasets/lemke-partial-discharge-measurements | Lab-controlled material-level PD data. Niche but ASCII format is trivial to work with. Good for understanding how insulation degradation manifests. | polyethylene cable
17 | TU Delft — GIS PD Interference Discrimination | TU Delft. European EMPIR FutureEnergy project. | PD vs interference in gas-insulated systems | Electric + magnetic sensors for GIS | Not specified | Not specified | Not specified | PD and interference/noise discrimination data from gas-insulated switchgear. Electric and magnetic sensor channels. Useful for understanding interference rejection methodology from a leading PD research group. | Not specified | Open access | CC BY 4.0 | https://data.mendeley.com/datasets/mmbgn94f4j/2 | GIS-specific (not transformer). Useful for interference/noise discrimination techniques. From top PD research group. | Gas-Insulated Systems
18 | TU Delft — Magnetic Loop Antenna Characterization (Zenodo) | TU Delft. IEEE Sensors Journal. DOI: 10.1109/JSEN.2021.3089084 | Sensor characterization (not PD classification) | Magnetic loop antenna for GIS PD measurements | N/A (characterization data) * over 80 depending on the figure | Characterization measurements | Not specified | Antenna characterization and calibration data for a magnetic loop antenna designed for PD measurements. Frequency response, sensitivity, and coupling characteristics. Reference for antenna-based PD sensor design. | Small | Open access | CC BY 4.0 | https://zenodo.org/record/5913233 | Sensor characterization, not classification. Reference for antenna-based PD measurement design. | Gas Insulated Substations
19 | Kaggle — Partial Discharge JPG Signals | Kaggle (Pletzer) | PD vs no-PD (visual plots) | Various | N/A (image plots) | Image collection | .jpg images | JPG image files showing plotted electrical signal waveforms — some with PD events visible, some without. NOT raw numerical data; these are screenshots/exports of oscilloscope or software plots. Only useful for visual reference or image-based classification PoC. | Small | Free, open | Kaggle terms | https://www.kaggle.com/datasets/pletzer/partial-discharge-jpg-signals | Low priority. Visual reference only. Could be used for quick image-based classifier proof of concept.
20 | GitHub — PD Localization in Transformer Tanks (Simulation) | Farzinkh et al., Nature Scientific Reports (2024). MIT license, 33 stars. | PD localization (x,y,z coordinates), not type classification | Simulated EM (COMSOL models) | Simulation-dependent | Multiple case studies: varying sensor position, frequency, tank size | Python scripts + CSV data files | COMSOL finite-element simulation outputs of EM wave propagation from PD sources inside transformer tank models. CSV files with signal features. Full ML pipeline code (SVR, XGBoost, BPNN, CNN) included. CNN achieves <17 cm localization error. | Not specified | Open (GitHub) | MIT | https://github.com/Farzinkh/Partial_Discharge | Simulation-based but methodology for PD signal processing in transformer tanks is directly applicable. Includes working ML code to adapt. Good reference for Phase 5 model selection. | power transformer tank
21 | GitHub PD Repos (PDAutoClust, PD-SVM) | Various researchers. PDAutoClust: IEEE Trans AI (2023), GPL-3.0. PD-SVM: community. | PRPD features with multi-class labels | Various | N/A (extracted features) | PDAutoClust: 4 datasets. PD-SVM: 1 dataset. | .txt and .csv (tabular features) | Pre-extracted 2D PRPD features (e.g., phase angle, charge magnitude, statistical features) with class labels. NOT raw waveforms. TXT/CSV tabular format for direct use in classical ML (SVM, clustering, random forest). | Small | Open (GitHub) | GPL-3.0 / unspecified | https://github.com/drarahman/PDAutoClust https://github.com/Tedgoo/Partial-Discharge-SVM | Good for PRPD pattern clustering and SVM benchmarking. Not raw waveforms.
22 | EMPIR Reference PD Test Cells (Zenodo) | European EMPIR 15NRM02-UHV project. DOI: 10.5281/zenodo.1476822 | Standardized PD generation (calibration/reference) | Reference test cells | N/A | Design + characterization data | Not specified | Test cell design specifications and characterization data for generating standardized, repeatable PD series. Calibration-oriented — useful for understanding how standardized PD benchmarks are created, not for direct ML training. | Small | Open access | CC BY 4.0 (assumed, Zenodo) | https://zenodo.org/records/1476822 | Calibration/reference oriented. Useful for understanding standardized PD generation methodology.
23 | DecPD: CNN-LSTM for PD Pattern Recognition (Paper Only) | MDPI Energies 18(23), 6245 | 6 defect types + 2 environmental noise types | HFCT, 100 MS/s oscilloscope | 100 MS/s (20 ms windows, 120k points) | N/A — no downloadable dataset | N/A (paper/methodology only) | PAPER ONLY — no downloadable data. Describes dual-channel CNN-LSTM architecture for temporal + spatial feature extraction from HFCT waveforms. Strong candidate architecture for Phase 5 model selection. | N/A | Open access (MDPI) | CC BY | https://www.mdpi.com/1996-1073/18/23/6245 | Architecture reference: CNN-LSTM for HFCT PD signals. Strong candidate for Phase 5.
24 | Acoustic-VMD + CNN-LSTM for Transformer PD (Paper Only) | PLOS ONE | Multi-source defect classification | Acoustic | N/A | N/A — no downloadable dataset | N/A (paper/methodology only) | PAPER ONLY — no downloadable data. Demonstrates VMD (Variational Mode Decomposition) preprocessing achieving 96.2% accuracy. VMD could be valuable for Phase 3 noise floor analysis. | N/A | Open access (PLOS ONE) | CC BY | https://journals.plos.org/plosone/article?id=10.1371/journal.pone.0335447 | Methodology reference: VMD preprocessing for noise analysis. 96.2% classification accuracy.
25 | MobileNets CNN for PRPD Pattern Recognition (Paper Only) | MDPI Applied Sciences 11(15), 6984 | 4 defect models (lab-generated PRPD spectra) | Lab PRPD setup | N/A | N/A — no downloadable dataset | N/A (paper/methodology only) | PAPER ONLY — no downloadable data. Lightweight CNN for real-time PD classification on edge devices. Directly relevant to Magnefy's goal of edge processing. | N/A | Open access (MDPI) | CC BY | https://www.mdpi.com/2076-3417/11/15/6984 | Edge deployment reference: lightweight CNN for real-time classification. Matches Magnefy's eventual edge goal.
26 | 2024 MDPI Systematic Review of PD Classification (Paper Only) | MDPI (2024 systematic review of 81 papers) | Survey of all PD classification approaches | Survey (all types) | N/A | 81 papers reviewed | N/A (paper/methodology only) | PAPER ONLY — no downloadable data. Key finding: 60% of PD classification studies used artificial lab defects and most did not share data publicly. Confirms scarcity of open PD datasets. | N/A | Open access (MDPI) | CC BY | N/A (search MDPI for 2024 PD classification review) | Validates the team's data scarcity challenge. Worth citing in project documentation.